## Control_Inputs
| Variable names | Description | Unit | Range | Category
1 | hvac_floor1_TSupAirSet_u | Supply air temperature setpoint for AHU | K | 285.15-313.15 | AHU
2 | hvac_floor1_TSupAirSet_activate | Activation for Supply air temperature setpoint for AHU | Boolean | [0,1] | AHU
3 | hvac_floor1_dpSet_u | Supply duct pressure setpoint for AHU | Pa | 50.0-410.0 | AHU
4 | hvac_floor1_dpSet_activate | Activation for Supply duct pressure setpoint for AHU | Boolean | [0,1] | AHU
5 | hvac_floor1_duaFanAirHanUnit_cooCoil_yCoo_u | Cooling coil valve control signal for AHU | 1 | 0.0-1.0 | AHU
6 | hvac_floor1_duaFanAirHanUnit_cooCoil_yCoo_activate | Activation for Cooling coil valve control signal for AHU | Boolean | [0,1] | AHU
7 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yEA_u | Exhaust air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
8 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yEA_activate | Activation for Exhaust air damper position setpoint for AHU | Boolean | [0,1] | AHU
9 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yOA_u | Outside air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
10 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yOA_activate | Activation for Outside air damper position setpoint for AHU | Boolean | [0,1] | AHU
11 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yRet_u | Return air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
12 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yRet_activate | Activation for Return air damper position setpoint for AHU | Boolean | [0,1] | AHU
13 | hvac_floor1_duaFanAirHanUnit_oveSpeRetFan_u | AHU return fan speed control signal | 1 | 0.0-1.0 | AHU
14 | hvac_floor1_duaFanAirHanUnit_oveSpeRetFan_activate | Activation for AHU return fan speed control signal | Boolean | [0,1] | AHU
15 | hvac_floor1_duaFanAirHanUnit_supFan_oveSpeSupFan_u | AHU supply fan speed control signal | 1 | 0.0-1.0 | AHU
16 | hvac_floor1_duaFanAirHanUnit_supFan_oveSpeSupFan_activate | Activation for AHU supply fan speed control signal | Boolean | [0,1] | AHU
17 | hvac_floor1_fivZonVAV_vAV1_oveZonLoc_yDam_u | Damper position setpoint for zone cor | 1 | 0.0-1.0 | Zone Terminal
18 | hvac_floor1_fivZonVAV_vAV1_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone cor | Boolean | [0,1] | Zone Terminal
19 | hvac_floor1_fivZonVAV_vAV1_oveZonLoc_yReaHea_u | Reheat control signal for zone cor | 1 | 0.0-1.0 | Zone Terminal
20 | hvac_floor1_fivZonVAV_vAV1_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone cor | Boolean | [0,1] | Zone Terminal
21 | hvac_floor1_fivZonVAV_vAV2_oveZonLoc_yDam_u | Damper position setpoint for zone sou | 1 | 0.0-1.0 | Zone Terminal
22 | hvac_floor1_fivZonVAV_vAV2_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone sou | Boolean | [0,1] | Zone Terminal
23 | hvac_floor1_fivZonVAV_vAV2_oveZonLoc_yReaHea_u | Reheat control signal for zone sou | 1 | 0.0-1.0 | Zone Terminal
24 | hvac_floor1_fivZonVAV_vAV2_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone sou | Boolean | [0,1] | Zone Terminal
25 | hvac_floor1_fivZonVAV_vAV3_oveZonLoc_yDam_u | Damper position setpoint for zone eas | 1 | 0.0-1.0 | Zone Terminal
26 | hvac_floor1_fivZonVAV_vAV3_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone eas | Boolean | [0,1] | Zone Terminal
27 | hvac_floor1_fivZonVAV_vAV3_oveZonLoc_yReaHea_u | Reheat control signal for zone eas | 1 | 0.0-1.0 | Zone Terminal
28 | hvac_floor1_fivZonVAV_vAV3_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone eas | Boolean | [0,1] | Zone Terminal
29 | hvac_floor1_fivZonVAV_vAV4_oveZonLoc_yDam_u | Damper position setpoint for zone nor | 1 | 0.0-1.0 | Zone Terminal
30 | hvac_floor1_fivZonVAV_vAV4_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone nor | Boolean | [0,1] | Zone Terminal
31 | hvac_floor1_fivZonVAV_vAV4_oveZonLoc_yReaHea_u | Reheat control signal for zone nor | 1 | 0.0-1.0 | Zone Terminal
32 | hvac_floor1_fivZonVAV_vAV4_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone nor | Boolean | [0,1] | Zone Terminal
33 | hvac_floor1_fivZonVAV_vAV5_oveZonLoc_yDam_u | Damper position setpoint for zone wes | 1 | 0.0-1.0 | Zone Terminal
34 | hvac_floor1_fivZonVAV_vAV5_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone wes | Boolean | [0,1] | Zone Terminal
35 | hvac_floor1_fivZonVAV_vAV5_oveZonLoc_yReaHea_u | Reheat control signal for zone wes | 1 | 0.0-1.0 | Zone Terminal
36 | hvac_floor1_fivZonVAV_vAV5_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone wes | Boolean | [0,1] | Zone Terminal
37 | hvac_floor1_oveZonCor_TZonCooSet_u | Zone air temperature cooling setpoint for zone cor | K | 285.15-313.15 | Zone Terminal
38 | hvac_floor1_oveZonCor_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone cor | Boolean | [0,1] | Zone Terminal
39 | hvac_floor1_oveZonCor_TZonHeaSet_u | Zone air temperature heating setpoint for zone cor | K | 285.15-313.15 | Zone Terminal
40 | hvac_floor1_oveZonCor_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone cor | Boolean | [0,1] | Zone Terminal
41 | hvac_floor1_oveZonEas_TZonCooSet_u | Zone air temperature cooling setpoint for zone eas | K | 285.15-313.15 | Zone Terminal
42 | hvac_floor1_oveZonEas_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone eas | Boolean | [0,1] | Zone Terminal
43 | hvac_floor1_oveZonEas_TZonHeaSet_u | Zone air temperature heating setpoint for zone eas | K | 285.15-313.15 | Zone Terminal
44 | hvac_floor1_oveZonEas_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone eas | Boolean | [0,1] | Zone Terminal
45 | hvac_floor1_oveZonNor_TZonCooSet_u | Zone air temperature cooling setpoint for zone nor | K | 285.15-313.15 | Zone Terminal
46 | hvac_floor1_oveZonNor_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone nor | Boolean | [0,1] | Zone Terminal
47 | hvac_floor1_oveZonNor_TZonHeaSet_u | Zone air temperature heating setpoint for zone nor | K | 285.15-313.15 | Zone Terminal
48 | hvac_floor1_oveZonNor_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone nor | Boolean | [0,1] | Zone Terminal
49 | hvac_floor1_oveZonSou_TZonCooSet_u | Zone air temperature cooling setpoint for zone sou | K | 285.15-313.15 | Zone Terminal
50 | hvac_floor1_oveZonSou_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone sou | Boolean | [0,1] | Zone Terminal
51 | hvac_floor1_oveZonSou_TZonHeaSet_u | Zone air temperature heating setpoint for zone sou | K | 285.15-313.15 | Zone Terminal
52 | hvac_floor1_oveZonSou_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone sou | Boolean | [0,1] | Zone Terminal
53 | hvac_floor1_oveZonWes_TZonCooSet_u | Zone air temperature cooling setpoint for zone wes | K | 285.15-313.15 | Zone Terminal
54 | hvac_floor1_oveZonWes_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone wes | Boolean | [0,1] | Zone Terminal
55 | hvac_floor1_oveZonWes_TZonHeaSet_u | Zone air temperature heating setpoint for zone wes | K | 285.15-313.15 | Zone Terminal
56 | hvac_floor1_oveZonWes_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone wes | Boolean | [0,1] | Zone Terminal
57 | hvac_floor2_TSupAirSet_u | Supply air temperature setpoint for AHU | K | 285.15-313.15 | AHU
58 | hvac_floor2_TSupAirSet_activate | Activation for Supply air temperature setpoint for AHU | Boolean | [0,1] | AHU
59 | hvac_floor2_dpSet_u | Supply duct pressure setpoint for AHU | Pa | 50.0-410.0 | AHU
60 | hvac_floor2_dpSet_activate | Activation for Supply duct pressure setpoint for AHU | Boolean | [0,1] | AHU
61 | hvac_floor2_duaFanAirHanUnit_cooCoil_yCoo_u | Cooling coil valve control signal for AHU | 1 | 0.0-1.0 | AHU
62 | hvac_floor2_duaFanAirHanUnit_cooCoil_yCoo_activate | Activation for Cooling coil valve control signal for AHU | Boolean | [0,1] | AHU
63 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yEA_u | Exhaust air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
64 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yEA_activate | Activation for Exhaust air damper position setpoint for AHU | Boolean | [0,1] | AHU
65 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yOA_u | Outside air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
66 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yOA_activate | Activation for Outside air damper position setpoint for AHU | Boolean | [0,1] | AHU
67 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yRet_u | Return air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
68 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yRet_activate | Activation for Return air damper position setpoint for AHU | Boolean | [0,1] | AHU
69 | hvac_floor2_duaFanAirHanUnit_oveSpeRetFan_u | AHU return fan speed control signal | 1 | 0.0-1.0 | AHU
70 | hvac_floor2_duaFanAirHanUnit_oveSpeRetFan_activate | Activation for AHU return fan speed control signal | Boolean | [0,1] | AHU
71 | hvac_floor2_duaFanAirHanUnit_supFan_oveSpeSupFan_u | AHU supply fan speed control signal | 1 | 0.0-1.0 | AHU
72 | hvac_floor2_duaFanAirHanUnit_supFan_oveSpeSupFan_activate | Activation for AHU supply fan speed control signal | Boolean | [0,1] | AHU
73 | hvac_floor2_fivZonVAV_vAV1_oveZonLoc_yDam_u | Damper position setpoint for zone cor | 1 | 0.0-1.0 | Zone Terminal
74 | hvac_floor2_fivZonVAV_vAV1_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone cor | Boolean | [0,1] | Zone Terminal
75 | hvac_floor2_fivZonVAV_vAV1_oveZonLoc_yReaHea_u | Reheat control signal for zone cor | 1 | 0.0-1.0 | Zone Terminal
76 | hvac_floor2_fivZonVAV_vAV1_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone cor | Boolean | [0,1] | Zone Terminal
77 | hvac_floor2_fivZonVAV_vAV2_oveZonLoc_yDam_u | Damper position setpoint for zone sou | 1 | 0.0-1.0 | Zone Terminal
78 | hvac_floor2_fivZonVAV_vAV2_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone sou | Boolean | [0,1] | Zone Terminal
79 | hvac_floor2_fivZonVAV_vAV2_oveZonLoc_yReaHea_u | Reheat control signal for zone sou | 1 | 0.0-1.0 | Zone Terminal
80 | hvac_floor2_fivZonVAV_vAV2_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone sou | Boolean | [0,1] | Zone Terminal
81 | hvac_floor2_fivZonVAV_vAV3_oveZonLoc_yDam_u | Damper position setpoint for zone eas | 1 | 0.0-1.0 | Zone Terminal
82 | hvac_floor2_fivZonVAV_vAV3_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone eas | Boolean | [0,1] | Zone Terminal
83 | hvac_floor2_fivZonVAV_vAV3_oveZonLoc_yReaHea_u | Reheat control signal for zone eas | 1 | 0.0-1.0 | Zone Terminal
84 | hvac_floor2_fivZonVAV_vAV3_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone eas | Boolean | [0,1] | Zone Terminal
85 | hvac_floor2_fivZonVAV_vAV4_oveZonLoc_yDam_u | Damper position setpoint for zone nor | 1 | 0.0-1.0 | Zone Terminal
86 | hvac_floor2_fivZonVAV_vAV4_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone nor | Boolean | [0,1] | Zone Terminal
87 | hvac_floor2_fivZonVAV_vAV4_oveZonLoc_yReaHea_u | Reheat control signal for zone nor | 1 | 0.0-1.0 | Zone Terminal
88 | hvac_floor2_fivZonVAV_vAV4_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone nor | Boolean | [0,1] | Zone Terminal
89 | hvac_floor2_fivZonVAV_vAV5_oveZonLoc_yDam_u | Damper position setpoint for zone wes | 1 | 0.0-1.0 | Zone Terminal
90 | hvac_floor2_fivZonVAV_vAV5_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone wes | Boolean | [0,1] | Zone Terminal
91 | hvac_floor2_fivZonVAV_vAV5_oveZonLoc_yReaHea_u | Reheat control signal for zone wes | 1 | 0.0-1.0 | Zone Terminal
92 | hvac_floor2_fivZonVAV_vAV5_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone wes | Boolean | [0,1] | Zone Terminal
93 | hvac_floor2_oveZonCor_TZonCooSet_u | Zone air temperature cooling setpoint for zone cor | K | 285.15-313.15 | Zone Terminal
94 | hvac_floor2_oveZonCor_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone cor | Boolean | [0,1] | Zone Terminal
95 | hvac_floor2_oveZonCor_TZonHeaSet_u | Zone air temperature heating setpoint for zone cor | K | 285.15-313.15 | Zone Terminal
96 | hvac_floor2_oveZonCor_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone cor | Boolean | [0,1] | Zone Terminal
97 | hvac_floor2_oveZonEas_TZonCooSet_u | Zone air temperature cooling setpoint for zone eas | K | 285.15-313.15 | Zone Terminal
98 | hvac_floor2_oveZonEas_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone eas | Boolean | [0,1] | Zone Terminal
99 | hvac_floor2_oveZonEas_TZonHeaSet_u | Zone air temperature heating setpoint for zone eas | K | 285.15-313.15 | Zone Terminal
100 | hvac_floor2_oveZonEas_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone eas | Boolean | [0,1] | Zone Terminal
101 | hvac_floor2_oveZonNor_TZonCooSet_u | Zone air temperature cooling setpoint for zone nor | K | 285.15-313.15 | Zone Terminal
102 | hvac_floor2_oveZonNor_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone nor | Boolean | [0,1] | Zone Terminal
103 | hvac_floor2_oveZonNor_TZonHeaSet_u | Zone air temperature heating setpoint for zone nor | K | 285.15-313.15 | Zone Terminal
104 | hvac_floor2_oveZonNor_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone nor | Boolean | [0,1] | Zone Terminal
105 | hvac_floor2_oveZonSou_TZonCooSet_u | Zone air temperature cooling setpoint for zone sou | K | 285.15-313.15 | Zone Terminal
106 | hvac_floor2_oveZonSou_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone sou | Boolean | [0,1] | Zone Terminal
107 | hvac_floor2_oveZonSou_TZonHeaSet_u | Zone air temperature heating setpoint for zone sou | K | 285.15-313.15 | Zone Terminal
108 | hvac_floor2_oveZonSou_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone sou | Boolean | [0,1] | Zone Terminal
109 | hvac_floor2_oveZonWes_TZonCooSet_u | Zone air temperature cooling setpoint for zone wes | K | 285.15-313.15 | Zone Terminal
110 | hvac_floor2_oveZonWes_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone wes | Boolean | [0,1] | Zone Terminal
111 | hvac_floor2_oveZonWes_TZonHeaSet_u | Zone air temperature heating setpoint for zone wes | K | 285.15-313.15 | Zone Terminal
112 | hvac_floor2_oveZonWes_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone wes | Boolean | [0,1] | Zone Terminal
113 | hvac_floor3_TSupAirSet_u | Supply air temperature setpoint for AHU | K | 285.15-313.15 | AHU
114 | hvac_floor3_TSupAirSet_activate | Activation for Supply air temperature setpoint for AHU | Boolean | [0,1] | AHU
115 | hvac_floor3_dpSet_u | Supply duct pressure setpoint for AHU | Pa | 50.0-410.0 | AHU
116 | hvac_floor3_dpSet_activate | Activation for Supply duct pressure setpoint for AHU | Boolean | [0,1] | AHU
117 | hvac_floor3_duaFanAirHanUnit_cooCoil_yCoo_u | Cooling coil valve control signal for AHU | 1 | 0.0-1.0 | AHU
118 | hvac_floor3_duaFanAirHanUnit_cooCoil_yCoo_activate | Activation for Cooling coil valve control signal for AHU | Boolean | [0,1] | AHU
119 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yEA_u | Exhaust air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
120 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yEA_activate | Activation for Exhaust air damper position setpoint for AHU | Boolean | [0,1] | AHU
121 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yOA_u | Outside air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
122 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yOA_activate | Activation for Outside air damper position setpoint for AHU | Boolean | [0,1] | AHU
123 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yRet_u | Return air damper position setpoint for AHU | 1 | 0.0-1.0 | AHU
124 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yRet_activate | Activation for Return air damper position setpoint for AHU | Boolean | [0,1] | AHU
125 | hvac_floor3_duaFanAirHanUnit_oveSpeRetFan_u | AHU return fan speed control signal | 1 | 0.0-1.0 | AHU
126 | hvac_floor3_duaFanAirHanUnit_oveSpeRetFan_activate | Activation for AHU return fan speed control signal | Boolean | [0,1] | AHU
127 | hvac_floor3_duaFanAirHanUnit_supFan_oveSpeSupFan_u | AHU supply fan speed control signal | 1 | 0.0-1.0 | AHU
128 | hvac_floor3_duaFanAirHanUnit_supFan_oveSpeSupFan_activate | Activation for AHU supply fan speed control signal | Boolean | [0,1] | AHU
129 | hvac_floor3_fivZonVAV_vAV1_oveZonLoc_yDam_u | Damper position setpoint for zone cor | 1 | 0.0-1.0 | Zone Terminal
130 | hvac_floor3_fivZonVAV_vAV1_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone cor | Boolean | [0,1] | Zone Terminal
131 | hvac_floor3_fivZonVAV_vAV1_oveZonLoc_yReaHea_u | Reheat control signal for zone cor | 1 | 0.0-1.0 | Zone Terminal
132 | hvac_floor3_fivZonVAV_vAV1_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone cor | Boolean | [0,1] | Zone Terminal
133 | hvac_floor3_fivZonVAV_vAV2_oveZonLoc_yDam_u | Damper position setpoint for zone sou | 1 | 0.0-1.0 | Zone Terminal
134 | hvac_floor3_fivZonVAV_vAV2_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone sou | Boolean | [0,1] | Zone Terminal
135 | hvac_floor3_fivZonVAV_vAV2_oveZonLoc_yReaHea_u | Reheat control signal for zone sou | 1 | 0.0-1.0 | Zone Terminal
136 | hvac_floor3_fivZonVAV_vAV2_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone sou | Boolean | [0,1] | Zone Terminal
137 | hvac_floor3_fivZonVAV_vAV3_oveZonLoc_yDam_u | Damper position setpoint for zone eas | 1 | 0.0-1.0 | Zone Terminal
138 | hvac_floor3_fivZonVAV_vAV3_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone eas | Boolean | [0,1] | Zone Terminal
139 | hvac_floor3_fivZonVAV_vAV3_oveZonLoc_yReaHea_u | Reheat control signal for zone eas | 1 | 0.0-1.0 | Zone Terminal
140 | hvac_floor3_fivZonVAV_vAV3_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone eas | Boolean | [0,1] | Zone Terminal
141 | hvac_floor3_fivZonVAV_vAV4_oveZonLoc_yDam_u | Damper position setpoint for zone nor | 1 | 0.0-1.0 | Zone Terminal
142 | hvac_floor3_fivZonVAV_vAV4_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone nor | Boolean | [0,1] | Zone Terminal
143 | hvac_floor3_fivZonVAV_vAV4_oveZonLoc_yReaHea_u | Reheat control signal for zone nor | 1 | 0.0-1.0 | Zone Terminal
144 | hvac_floor3_fivZonVAV_vAV4_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone nor | Boolean | [0,1] | Zone Terminal
145 | hvac_floor3_fivZonVAV_vAV5_oveZonLoc_yDam_u | Damper position setpoint for zone wes | 1 | 0.0-1.0 | Zone Terminal
146 | hvac_floor3_fivZonVAV_vAV5_oveZonLoc_yDam_activate | Activation for Damper position setpoint for zone wes | Boolean | [0,1] | Zone Terminal
147 | hvac_floor3_fivZonVAV_vAV5_oveZonLoc_yReaHea_u | Reheat control signal for zone wes | 1 | 0.0-1.0 | Zone Terminal
148 | hvac_floor3_fivZonVAV_vAV5_oveZonLoc_yReaHea_activate | Activation for Reheat control signal for zone wes | Boolean | [0,1] | Zone Terminal
149 | hvac_floor3_oveZonCor_TZonCooSet_u | Zone air temperature cooling setpoint for zone cor | K | 285.15-313.15 | Zone Terminal
150 | hvac_floor3_oveZonCor_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone cor | Boolean | [0,1] | Zone Terminal
151 | hvac_floor3_oveZonCor_TZonHeaSet_u | Zone air temperature heating setpoint for zone cor | K | 285.15-313.15 | Zone Terminal
152 | hvac_floor3_oveZonCor_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone cor | Boolean | [0,1] | Zone Terminal
153 | hvac_floor3_oveZonEas_TZonCooSet_u | Zone air temperature cooling setpoint for zone eas | K | 285.15-313.15 | Zone Terminal
154 | hvac_floor3_oveZonEas_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone eas | Boolean | [0,1] | Zone Terminal
155 | hvac_floor3_oveZonEas_TZonHeaSet_u | Zone air temperature heating setpoint for zone eas | K | 285.15-313.15 | Zone Terminal
156 | hvac_floor3_oveZonEas_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone eas | Boolean | [0,1] | Zone Terminal
157 | hvac_floor3_oveZonNor_TZonCooSet_u | Zone air temperature cooling setpoint for zone nor | K | 285.15-313.15 | Zone Terminal
158 | hvac_floor3_oveZonNor_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone nor | Boolean | [0,1] | Zone Terminal
159 | hvac_floor3_oveZonNor_TZonHeaSet_u | Zone air temperature heating setpoint for zone nor | K | 285.15-313.15 | Zone Terminal
160 | hvac_floor3_oveZonNor_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone nor | Boolean | [0,1] | Zone Terminal
161 | hvac_floor3_oveZonSou_TZonCooSet_u | Zone air temperature cooling setpoint for zone sou | K | 285.15-313.15 | Zone Terminal
162 | hvac_floor3_oveZonSou_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone sou | Boolean | [0,1] | Zone Terminal
163 | hvac_floor3_oveZonSou_TZonHeaSet_u | Zone air temperature heating setpoint for zone sou | K | 285.15-313.15 | Zone Terminal
164 | hvac_floor3_oveZonSou_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone sou | Boolean | [0,1] | Zone Terminal
165 | hvac_floor3_oveZonWes_TZonCooSet_u | Zone air temperature cooling setpoint for zone wes | K | 285.15-313.15 | Zone Terminal
166 | hvac_floor3_oveZonWes_TZonCooSet_activate | Activation for Zone air temperature cooling setpoint for zone wes | Boolean | [0,1] | Zone Terminal
167 | hvac_floor3_oveZonWes_TZonHeaSet_u | Zone air temperature heating setpoint for zone wes | K | 285.15-313.15 | Zone Terminal
168 | hvac_floor3_oveZonWes_TZonHeaSet_activate | Activation for Zone air temperature heating setpoint for zone wes | Boolean | [0,1] | Zone Terminal
169 | hvac_oveChiWatSys_TW_set_u | Chilled/hot water supply setpoint | K | 278.15-288.15 | Water Side
170 | hvac_oveChiWatSys_TW_set_activate | Activation for Chilled/hot water supply setpoint | Boolean | [0,1] | Water Side
171 | hvac_oveChiWatSys_dp_set_u | Differential pressure setpoint | Pa | 0.0-19130000.0 | Water Side
172 | hvac_oveChiWatSys_dp_set_activate | Activation for Differential pressure setpoint | Boolean | [0,1] | Water Side
173 | hvac_oveHotWatSys_TW_set_u | Chilled/hot water supply setpoint | K | 291.15-353.15 | Water Side
174 | hvac_oveHotWatSys_TW_set_activate | Activation for Chilled/hot water supply setpoint | Boolean | [0,1] | Water Side
175 | hvac_oveHotWatSys_dp_set_u | Differential pressure setpoint | Pa | 0.0-19130000.0 | Water Side
176 | hvac_oveHotWatSys_dp_set_activate | Activation for Differential pressure setpoint | Boolean | [0,1] | Water Side

## Output_Measurement
| Variable names | Description | Unit | Category
1 | hvac_floor1_reaZonCor_TRoo_Coo_set_y | Zone temperature cooling setpoint for zone cor | K | Zone Terminal
2 | hvac_floor1_reaZonCor_TRoo_Hea_set_y | Zone temperature heating setpoint for zone cor | K | Zone Terminal
3 | hvac_floor1_reaZonCor_TSup_y | Discharge air temperature to zone measurement for zone cor | K | Zone Terminal
4 | hvac_floor1_reaZonCor_TZon_y | Zone air temperature measurement for zone cor | K | Zone Terminal
5 | hvac_floor1_reaZonCor_V_flow_y | Discharge air flowrate to zone measurement for zone cor | m3/s | Zone Terminal
6 | hvac_floor1_reaZonCor_V_flow_set_y | Airflow setpointcor | m3/s | Zone Terminal
7 | hvac_floor1_reaZonCor_yCoo_y | Cooling PID signal measurement for zone cor | 1 | Zone Terminal
8 | hvac_floor1_reaZonCor_yDam_y | Damper position measurement for zone cor | 1 | Zone Terminal
9 | hvac_floor1_reaZonCor_yHea_y | Heating PID signal measurement for zone cor | 1 | Zone Terminal
10 | hvac_floor1_reaZonCor_yReheaVal_y | Reheat valve position measurement for zone cor | 1 | Zone Terminal
11 | hvac_floor1_reaZonEas_TRoo_Coo_set_y | Zone temperature cooling setpoint for zoneeas | K | Zone Terminal
12 | hvac_floor1_reaZonEas_TRoo_Hea_set_y | Zone temperature heating setpoint for zone eas | K | Zone Terminal
13 | hvac_floor1_reaZonEas_TSup_y | Discharge air temperature to zone measurement for zone eas | K | Zone Terminal
14 | hvac_floor1_reaZonEas_TZon_y | Zone air temperature measurement for zone eas | K | Zone Terminal
15 | hvac_floor1_reaZonEas_V_flow_y | Discharge air flowrate to zone measurement for zone eas | m3/s | Zone Terminal
16 | hvac_floor1_reaZonEas_V_flow_set_y | Airflow setpointeas | m3/s | Zone Terminal
17 | hvac_floor1_reaZonEas_yCoo_y | Cooling PID signal measurement for zone eas | 1 | Zone Terminal
18 | hvac_floor1_reaZonEas_yDam_y | Damper position measurement for zone eas | 1 | Zone Terminal
19 | hvac_floor1_reaZonEas_yHea_y | Heating PID signal measurement for zone eas | 1 | Zone Terminal
20 | hvac_floor1_reaZonEas_yReheaVal_y | Reheat valve position measurement for zone eas | 1 | Zone Terminal
21 | hvac_floor1_reaZonNor_TRoo_Coo_set_y | Zone temperature cooling setpoint for zone cor | K | Zone Terminal
22 | hvac_floor1_reaZonNor_TRoo_Hea_set_y | Zone temperature heating setpoint for zone nor | K | Zone Terminal
23 | hvac_floor1_reaZonNor_TSup_y | Discharge air temperature to zone measurement for zone nor | K | Zone Terminal
24 | hvac_floor1_reaZonNor_TZon_y | Zone air temperature measurement for zone nor | K | Zone Terminal
25 | hvac_floor1_reaZonNor_V_flow_y | Discharge air flowrate to zone measurement for zone nor | m3/s | Zone Terminal
26 | hvac_floor1_reaZonNor_V_flow_set_y | Airflow setpointnor | m3/s | Zone Terminal
27 | hvac_floor1_reaZonNor_yCoo_y | Cooling PID signal measurement for zone nor | 1 | Zone Terminal
28 | hvac_floor1_reaZonNor_yDam_y | Damper position measurement for zone nor | 1 | Zone Terminal
29 | hvac_floor1_reaZonNor_yHea_y | Heating PID signal measurement for zone nor | 1 | Zone Terminal
30 | hvac_floor1_reaZonNor_yReheaVal_y | Reheat valve position measurement for zone nor | 1 | Zone Terminal
31 | hvac_floor1_reaZonSou_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonesou | K | Zone Terminal
32 | hvac_floor1_reaZonSou_TRoo_Hea_set_y | Zone temperature heating setpoint for zone sou | K | Zone Terminal
33 | hvac_floor1_reaZonSou_TSup_y | Discharge air temperature to zone measurement for zone sou | K | Zone Terminal
34 | hvac_floor1_reaZonSou_TZon_y | Zone air temperature measurement for zone sou | K | Zone Terminal
35 | hvac_floor1_reaZonSou_V_flow_y | Discharge air flowrate to zone measurement for zone sou | m3/s | Zone Terminal
36 | hvac_floor1_reaZonSou_V_flow_set_y | Airflow setpointsou | m3/s | Zone Terminal
37 | hvac_floor1_reaZonSou_yCoo_y | Cooling PID signal measurement for zone sou | 1 | Zone Terminal
38 | hvac_floor1_reaZonSou_yDam_y | Damper position measurement for zone sou | 1 | Zone Terminal
39 | hvac_floor1_reaZonSou_yHea_y | Heating PID signal measurement for zone sou | 1 | Zone Terminal
40 | hvac_floor1_reaZonSou_yReheaVal_y | Reheat valve position measurement for zone sou | 1 | Zone Terminal
41 | hvac_floor1_reaZonWes_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonewes | K | Zone Terminal
42 | hvac_floor1_reaZonWes_TRoo_Hea_set_y | Zone temperature heating setpoint for zone wes | K | Zone Terminal
43 | hvac_floor1_reaZonWes_TSup_y | Discharge air temperature to zone measurement for zone wes | K | Zone Terminal
44 | hvac_floor1_reaZonWes_TZon_y | Zone air temperature measurement for zone wes | K | Zone Terminal
45 | hvac_floor1_reaZonWes_V_flow_y | Discharge air flowrate to zone measurement for zone wes | m3/s | Zone Terminal
46 | hvac_floor1_reaZonWes_V_flow_set_y | Airflow setpointwes | m3/s | Zone Terminal
47 | hvac_floor1_reaZonWes_yCoo_y | Cooling PID signal measurement for zone wes | 1 | Zone Terminal
48 | hvac_floor1_reaZonWes_yDam_y | Damper position measurement for zone wes | 1 | Zone Terminal
49 | hvac_floor1_reaZonWes_yHea_y | Heating PID signal measurement for zone wes | 1 | Zone Terminal
50 | hvac_floor1_reaZonWes_yReheaVal_y | Reheat valve position measurement for zone wes | 1 | Zone Terminal
51 | hvac_floor1_readAhu_PFanSup_y | Electrical power measurement of supply fan for AHU | W | AHU
52 | hvac_floor1_readAhu_TCooCoiRet_y | Cooling coil return water temperature measurement for AHU | K | AHU
53 | hvac_floor1_readAhu_TCooCoiSup_y | Cooling coil supply water temperature measurement for AHU | K | AHU
54 | hvac_floor1_readAhu_TMix_y | Mixed air temperature measurement for AHU | K | AHU
55 | hvac_floor1_readAhu_TRet_y | Return air temperature measurement for AHU | K | AHU
56 | hvac_floor1_readAhu_TSup_y | Supply air temperature measurement for AHU | K | AHU
57 | hvac_floor1_readAhu_TSup_set_y | Supply air temperature setpoint measurement for AHU | K | AHU
58 | hvac_floor1_readAhu_V_flow_OA_y | Supply outdoor airflow rate measurement for AHU | m3/s | AHU
59 | hvac_floor1_readAhu_V_flow_ret_y | Return air flowrate measurement for AHU | m3/s | AHU
60 | hvac_floor1_readAhu_V_flow_sup_y | Supply air flowrate measurement for AHU | m3/s | AHU
61 | hvac_floor1_readAhu_dp_sup_y | Discharge pressure of supply fan for AHU | Pa | AHU
62 | hvac_floor1_readAhu_occ_y | Occupancy status (1 occupied, 0 unoccupied) | 1 | AHU
63 | hvac_floor1_readAhu_yCooVal_y | AHU cooling coil valve position measurement | 1 | AHU
64 | hvac_floor1_readAhu_yOA_y | AHU cooling coil valve position measurement | 1 | AHU
65 | hvac_floor2_reaZonCor_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonecor | K | Zone Terminal
66 | hvac_floor2_reaZonCor_TRoo_Hea_set_y | Zone temperature heating setpoint for zone cor | K | Zone Terminal
67 | hvac_floor2_reaZonCor_TSup_y | Discharge air temperature to zone measurement for zone cor | K | Zone Terminal
68 | hvac_floor2_reaZonCor_TZon_y | Zone air temperature measurement for zone cor | K | Zone Terminal
69 | hvac_floor2_reaZonCor_V_flow_y | Discharge air flowrate to zone measurement for zone cor | m3/s | Zone Terminal
70 | hvac_floor2_reaZonCor_V_flow_set_y | Airflow setpointcor | m3/s | Zone Terminal
71 | hvac_floor2_reaZonCor_yCoo_y | Cooling PID signal measurement for zone cor | 1 | Zone Terminal
72 | hvac_floor2_reaZonCor_yDam_y | Damper position measurement for zone cor | 1 | Zone Terminal
73 | hvac_floor2_reaZonCor_yHea_y | Heating PID signal measurement for zone cor | 1 | Zone Terminal
74 | hvac_floor2_reaZonCor_yReheaVal_y | Reheat valve position measurement for zone cor | 1 | Zone Terminal
75 | hvac_floor2_reaZonEas_TRoo_Coo_set_y | Zone temperature cooling setpoint for zoneeas | K | Zone Terminal
76 | hvac_floor2_reaZonEas_TRoo_Hea_set_y | Zone temperature heating setpoint for zone eas | K | Zone Terminal
77 | hvac_floor2_reaZonEas_TSup_y | Discharge air temperature to zone measurement for zone eas | K | Zone Terminal
78 | hvac_floor2_reaZonEas_TZon_y | Zone air temperature measurement for zone eas | K | Zone Terminal
79 | hvac_floor2_reaZonEas_V_flow_y | Discharge air flowrate to zone measurement for zone eas | m3/s | Zone Terminal
80 | hvac_floor2_reaZonEas_V_flow_set_y | Airflow setpointeas | m3/s | Zone Terminal
81 | hvac_floor2_reaZonEas_yCoo_y | Cooling PID signal measurement for zone eas | 1 | Zone Terminal
82 | hvac_floor2_reaZonEas_yDam_y | Damper position measurement for zone eas | 1 | Zone Terminal
83 | hvac_floor2_reaZonEas_yHea_y | Heating PID signal measurement for zone eas | 1 | Zone Terminal
84 | hvac_floor2_reaZonEas_yReheaVal_y | Reheat valve position measurement for zone eas | 1 | Zone Terminal
85 | hvac_floor2_reaZonNor_TRoo_Coo_set_y | Zone temperature cooling setpoint for zone cor | K | Zone Terminal
86 | hvac_floor2_reaZonNor_TRoo_Hea_set_y | Zone temperature heating setpoint for zone nor | K | Zone Terminal
87 | hvac_floor2_reaZonNor_TSup_y | Discharge air temperature to zone measurement for zone nor | K | Zone Terminal
88 | hvac_floor2_reaZonNor_TZon_y | Zone air temperature measurement for zone nor | K | Zone Terminal
89 | hvac_floor2_reaZonNor_V_flow_y | Discharge air flowrate to zone measurement for zone nor | m3/s | Zone Terminal
90 | hvac_floor2_reaZonNor_V_flow_set_y | Airflow setpointnor | m3/s | Zone Terminal
91 | hvac_floor2_reaZonNor_yCoo_y | Cooling PID signal measurement for zone nor | 1 | Zone Terminal
92 | hvac_floor2_reaZonNor_yDam_y | Damper position measurement for zone nor | 1 | Zone Terminal
93 | hvac_floor2_reaZonNor_yHea_y | Heating PID signal measurement for zone nor | 1 | Zone Terminal
94 | hvac_floor2_reaZonNor_yReheaVal_y | Reheat valve position measurement for zone nor | 1 | Zone Terminal
95 | hvac_floor2_reaZonSou_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonesou | K | Zone Terminal
96 | hvac_floor2_reaZonSou_TRoo_Hea_set_y | Zone temperature heating setpoint for zone sou | K | Zone Terminal
97 | hvac_floor2_reaZonSou_TSup_y | Discharge air temperature to zone measurement for zone sou | K | Zone Terminal
98 | hvac_floor2_reaZonSou_TZon_y | Zone air temperature measurement for zone sou | K | Zone Terminal
99 | hvac_floor2_reaZonSou_V_flow_y | Discharge air flowrate to zone measurement for zone sou | m3/s | Zone Terminal
100 | hvac_floor2_reaZonSou_V_flow_set_y | Airflow setpointsou | m3/s | Zone Terminal
101 | hvac_floor2_reaZonSou_yCoo_y | Cooling PID signal measurement for zone sou | 1 | Zone Terminal
102 | hvac_floor2_reaZonSou_yDam_y | Damper position measurement for zone sou | 1 | Zone Terminal
103 | hvac_floor2_reaZonSou_yHea_y | Heating PID signal measurement for zone sou | 1 | Zone Terminal
104 | hvac_floor2_reaZonSou_yReheaVal_y | Reheat valve position measurement for zone sou | 1 | Zone Terminal
105 | hvac_floor2_reaZonWes_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonewes | K | Zone Terminal
106 | hvac_floor2_reaZonWes_TRoo_Hea_set_y | Zone temperature heating setpoint for zone wes | K | Zone Terminal
107 | hvac_floor2_reaZonWes_TSup_y | Discharge air temperature to zone measurement for zone wes | K | Zone Terminal
108 | hvac_floor2_reaZonWes_TZon_y | Zone air temperature measurement for zone wes | K | Zone Terminal
109 | hvac_floor2_reaZonWes_V_flow_y | Discharge air flowrate to zone measurement for zone wes | m3/s | Zone Terminal
110 | hvac_floor2_reaZonWes_V_flow_set_y | Airflow setpointwes | m3/s | Zone Terminal
111 | hvac_floor2_reaZonWes_yCoo_y | Cooling PID signal measurement for zone wes | 1 | Zone Terminal
112 | hvac_floor2_reaZonWes_yDam_y | Damper position measurement for zone wes | 1 | Zone Terminal
113 | hvac_floor2_reaZonWes_yHea_y | Heating PID signal measurement for zone wes | 1 | Zone Terminal
114 | hvac_floor2_reaZonWes_yReheaVal_y | Reheat valve position measurement for zone wes | 1 | Zone Terminal
115 | hvac_floor2_readAhu_PFanSup_y | Electrical power measurement of supply fan for AHU | W | AHU
116 | hvac_floor2_readAhu_TCooCoiRet_y | Cooling coil return water temperature measurement for AHU | K | AHU
117 | hvac_floor2_readAhu_TCooCoiSup_y | Cooling coil supply water temperature measurement for AHU | K | AHU
118 | hvac_floor2_readAhu_TMix_y | Mixed air temperature measurement for AHU | K | AHU
119 | hvac_floor2_readAhu_TRet_y | Return air temperature measurement for AHU | K | AHU
120 | hvac_floor2_readAhu_TSup_y | Supply air temperature measurement for AHU | K | AHU
121 | hvac_floor2_readAhu_TSup_set_y | Supply air temperature setpoint measurement for AHU | K | AHU
122 | hvac_floor2_readAhu_V_flow_OA_y | Supply outdoor airflow rate measurement for AHU | m3/s | AHU
123 | hvac_floor2_readAhu_V_flow_ret_y | Return air flowrate measurement for AHU | m3/s | AHU
124 | hvac_floor2_readAhu_V_flow_sup_y | Supply air flowrate measurement for AHU | m3/s | AHU
125 | hvac_floor2_readAhu_dp_sup_y | Discharge pressure of supply fan for AHU | Pa | AHU
126 | hvac_floor2_readAhu_occ_y | Occupancy status (1 occupied, 0 unoccupied) | 1 | AHU
127 | hvac_floor2_readAhu_yCooVal_y | AHU cooling coil valve position measurement | 1 | AHU
128 | hvac_floor2_readAhu_yOA_y | AHU cooling coil valve position measurement | 1 | AHU
129 | hvac_floor3_reaZonCor_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonecor | K | Zone Terminal
130 | hvac_floor3_reaZonCor_TRoo_Hea_set_y | Zone temperature heating setpoint for zone cor | K | Zone Terminal
131 | hvac_floor3_reaZonCor_TSup_y | Discharge air temperature to zone measurement for zone cor | K | Zone Terminal
132 | hvac_floor3_reaZonCor_TZon_y | Zone air temperature measurement for zone cor | K | Zone Terminal
133 | hvac_floor3_reaZonCor_V_flow_y | Discharge air flowrate to zone measurement for zone cor | m3/s | Zone Terminal
134 | hvac_floor3_reaZonCor_V_flow_set_y | Airflow setpointcor | m3/s | Zone Terminal
135 | hvac_floor3_reaZonCor_yCoo_y | Cooling PID signal measurement for zone cor | 1 | Zone Terminal
136 | hvac_floor3_reaZonCor_yDam_y | Damper position measurement for zone cor | 1 | Zone Terminal
137 | hvac_floor3_reaZonCor_yHea_y | Heating PID signal measurement for zone cor | 1 | Zone Terminal
138 | hvac_floor3_reaZonCor_yReheaVal_y | Reheat valve position measurement for zone cor | 1 | Zone Terminal
139 | hvac_floor3_reaZonEas_TRoo_Coo_set_y | Zone temperature cooling setpoint for zoneeas | K | Zone Terminal
140 | hvac_floor3_reaZonEas_TRoo_Hea_set_y | Zone temperature heating setpoint for zone eas | K | Zone Terminal
141 | hvac_floor3_reaZonEas_TSup_y | Discharge air temperature to zone measurement for zone eas | K | Zone Terminal
142 | hvac_floor3_reaZonEas_TZon_y | Zone air temperature measurement for zone eas | K | Zone Terminal
143 | hvac_floor3_reaZonEas_V_flow_y | Discharge air flowrate to zone measurement for zone eas | m3/s | Zone Terminal
144 | hvac_floor3_reaZonEas_V_flow_set_y | Airflow setpointeas | m3/s | Zone Terminal
145 | hvac_floor3_reaZonEas_yCoo_y | Cooling PID signal measurement for zone eas | 1 | Zone Terminal
146 | hvac_floor3_reaZonEas_yDam_y | Damper position measurement for zone eas | 1 | Zone Terminal
147 | hvac_floor3_reaZonEas_yHea_y | Heating PID signal measurement for zone eas | 1 | Zone Terminal
148 | hvac_floor3_reaZonEas_yReheaVal_y | Reheat valve position measurement for zone eas | 1 | Zone Terminal
149 | hvac_floor3_reaZonNor_TRoo_Coo_set_y | Zone temperature cooling setpoint for zone cor | K | Zone Terminal
150 | hvac_floor3_reaZonNor_TRoo_Hea_set_y | Zone temperature heating setpoint for zone nor | K | Zone Terminal
151 | hvac_floor3_reaZonNor_TSup_y | Discharge air temperature to zone measurement for zone nor | K | Zone Terminal
152 | hvac_floor3_reaZonNor_TZon_y | Zone air temperature measurement for zone nor | K | Zone Terminal
153 | hvac_floor3_reaZonNor_V_flow_y | Discharge air flowrate to zone measurement for zone nor | m3/s | Zone Terminal
154 | hvac_floor3_reaZonNor_V_flow_set_y | Airflow setpointnor | m3/s | Zone Terminal
155 | hvac_floor3_reaZonNor_yCoo_y | Cooling PID signal measurement for zone nor | 1 | Zone Terminal
156 | hvac_floor3_reaZonNor_yDam_y | Damper position measurement for zone nor | 1 | Zone Terminal
157 | hvac_floor3_reaZonNor_yHea_y | Heating PID signal measurement for zone nor | 1 | Zone Terminal
158 | hvac_floor3_reaZonNor_yReheaVal_y | Reheat valve position measurement for zone nor | 1 | Zone Terminal
159 | hvac_floor3_reaZonSou_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonesou | K | Zone Terminal
160 | hvac_floor3_reaZonSou_TRoo_Hea_set_y | Zone temperature heating setpoint for zone sou | K | Zone Terminal
161 | hvac_floor3_reaZonSou_TSup_y | Discharge air temperature to zone measurement for zone sou | K | Zone Terminal
162 | hvac_floor3_reaZonSou_TZon_y | Zone air temperature measurement for zone sou | K | Zone Terminal
163 | hvac_floor3_reaZonSou_V_flow_y | Discharge air flowrate to zone measurement for zone sou | m3/s | Zone Terminal
164 | hvac_floor3_reaZonSou_V_flow_set_y | Airflow setpointsou | m3/s | Zone Terminal
165 | hvac_floor3_reaZonSou_yCoo_y | Cooling PID signal measurement for zone sou | 1 | Zone Terminal
166 | hvac_floor3_reaZonSou_yDam_y | Damper position measurement for zone sou | 1 | Zone Terminal
167 | hvac_floor3_reaZonSou_yHea_y | Heating PID signal measurement for zone sou | 1 | Zone Terminal
168 | hvac_floor3_reaZonSou_yReheaVal_y | Reheat valve position measurement for zone sou | 1 | Zone Terminal
169 | hvac_floor3_reaZonWes_TRoo_Coo_set_y | Zone temperature cooling setpoint for zonewes | K | Zone Terminal
170 | hvac_floor3_reaZonWes_TRoo_Hea_set_y | Zone temperature heating setpoint for zone wes | K | Zone Terminal
171 | hvac_floor3_reaZonWes_TSup_y | Discharge air temperature to zone measurement for zone wes | K | Zone Terminal
172 | hvac_floor3_reaZonWes_TZon_y | Zone air temperature measurement for zone wes | K | Zone Terminal
173 | hvac_floor3_reaZonWes_V_flow_y | Discharge air flowrate to zone measurement for zone wes | m3/s | Zone Terminal
174 | hvac_floor3_reaZonWes_V_flow_set_y | Airflow setpointwes | m3/s | Zone Terminal
175 | hvac_floor3_reaZonWes_yCoo_y | Cooling PID signal measurement for zone wes | 1 | Zone Terminal
176 | hvac_floor3_reaZonWes_yDam_y | Damper position measurement for zone wes | 1 | Zone Terminal
177 | hvac_floor3_reaZonWes_yHea_y | Heating PID signal measurement for zone wes | 1 | Zone Terminal
178 | hvac_floor3_reaZonWes_yReheaVal_y | Reheat valve position measurement for zone wes | 1 | Zone Terminal
179 | hvac_floor3_readAhu_PFanSup_y | Electrical power measurement of supply fan for AHU | W | AHU
180 | hvac_floor3_readAhu_TCooCoiRet_y | Cooling coil return water temperature measurement for AHU | K | AHU
181 | hvac_floor3_readAhu_TCooCoiSup_y | Cooling coil supply water temperature measurement for AHU | K | AHU
182 | hvac_floor3_readAhu_TMix_y | Mixed air temperature measurement for AHU | K | AHU
183 | hvac_floor3_readAhu_TRet_y | Return air temperature measurement for AHU | K | AHU
184 | hvac_floor3_readAhu_TSup_y | Supply air temperature measurement for AHU | K | AHU
185 | hvac_floor3_readAhu_TSup_set_y | Supply air temperature setpoint measurement for AHU | K | AHU
186 | hvac_floor3_readAhu_V_flow_OA_y | Supply outdoor airflow rate measurement for AHU | m3/s | AHU
187 | hvac_floor3_readAhu_V_flow_ret_y | Return air flowrate measurement for AHU | m3/s | AHU
188 | hvac_floor3_readAhu_V_flow_sup_y | Supply air flowrate measurement for AHU | m3/s | AHU
189 | hvac_floor3_readAhu_dp_sup_y | Discharge pressure of supply fan for AHU | Pa | AHU
190 | hvac_floor3_readAhu_occ_y | Occupancy status (1 occupied, 0 unoccupied) | 1 | AHU
191 | hvac_floor3_readAhu_yCooVal_y | AHU cooling coil valve position measurement | 1 | AHU
192 | hvac_floor3_readAhu_yOA_y | AHU cooling coil valve position measurement | 1 | AHU
193 | hvac_reaChiWatSys_TW_y | Chilled water temperature measurement | K | Water Side
194 | hvac_reaChiWatSys_dp_y | Differential pressure of chilled/hot water measurement | K | Water Side
195 | hvac_reaChiWatSys_reaPChi_y | Multiple chiller power consumption | W | Water Side
196 | hvac_reaChiWatSys_reaPCooTow_y | Multiple cooling tower power consumption | W | Water Side
197 | hvac_reaChiWatSys_reaPPum_y | Chilled water plant pump power consumption | W | Water Side
198 | hvac_reaHotWatSys_TW_y | Chilled water temperature measurement | K | Water Side
199 | hvac_reaHotWatSys_dp_y | Differential pressure of chilled/hot water measurement | K | Water Side
200 | hvac_reaHotWatSys_reaPBoi_y | Multiple gas power consumption | W | Water Side
201 | hvac_reaHotWatSys_reaPPum_y | Chilled water plant pump power consumption | W | Water Side
202 | loaEPlus_weatherStation_reaWeaCeiHei_y | Cloud cover ceiling height measurement | m | AHU
203 | loaEPlus_weatherStation_reaWeaCloTim_y | Day number with units of seconds | s | AHU
204 | loaEPlus_weatherStation_reaWeaHDifHor_y | Horizontal diffuse solar radiation measurement | W/m2 | AHU
205 | loaEPlus_weatherStation_reaWeaHDirNor_y | Direct normal radiation measurement | W/m2 | AHU
206 | loaEPlus_weatherStation_reaWeaHGloHor_y | Global horizontal solar irradiation measurement | W/m2 | AHU
207 | loaEPlus_weatherStation_reaWeaHHorIR_y | Horizontal infrared irradiation measurement | W/m2 | AHU
208 | loaEPlus_weatherStation_reaWeaLat_y | Latitude of the location | rad | AHU
209 | loaEPlus_weatherStation_reaWeaLon_y | Longitude of the location | rad | AHU
210 | loaEPlus_weatherStation_reaWeaNOpa_y | Opaque sky cover measurement | 1 | AHU
211 | loaEPlus_weatherStation_reaWeaNTot_y | Sky cover measurement | 1 | AHU
212 | loaEPlus_weatherStation_reaWeaPAtm_y | Atmospheric pressure measurement | Pa | AHU
213 | loaEPlus_weatherStation_reaWeaRelHum_y | Outside relative humidity measurement | 1 | AHU
214 | loaEPlus_weatherStation_reaWeaSolAlt_y | Solar altitude angle measurement | rad | AHU
215 | loaEPlus_weatherStation_reaWeaSolDec_y | Solar declination angle measurement | rad | AHU
216 | loaEPlus_weatherStation_reaWeaSolHouAng_y | Solar hour angle measurement | rad | AHU
217 | loaEPlus_weatherStation_reaWeaSolTim_y | Solar time | s | AHU
218 | loaEPlus_weatherStation_reaWeaSolZen_y | Solar zenith angle measurement | rad | AHU
219 | loaEPlus_weatherStation_reaWeaTBlaSky_y | Black-body sky temperature measurement | K | AHU
220 | loaEPlus_weatherStation_reaWeaTDewPoi_y | Dew point temperature measurement | K | AHU
221 | loaEPlus_weatherStation_reaWeaTDryBul_y | Outside drybulb temperature measurement | K | AHU
222 | loaEPlus_weatherStation_reaWeaTWetBul_y | Wet bulb temperature measurement | K | AHU
223 | loaEPlus_weatherStation_reaWeaWinDir_y | Wind direction measurement | rad | AHU
224 | loaEPlus_weatherStation_reaWeaWinSpe_y | Wind speed measurement | m/s | AHU
225 | hvac_floor1_TSupAirSet_y | Supply air temperature setpoint for AHU | K | AHU
226 | hvac_floor1_dpSet_y | Supply duct pressure setpoint for AHU | Pa | AHU
227 | hvac_floor1_duaFanAirHanUnit_cooCoil_yCoo_y | Cooling coil valve control signal for AHU | 1 | AHU
228 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yEA_y | Exhaust air damper position setpoint for AHU | 1 | AHU
229 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yOA_y | Outside air damper position setpoint for AHU | 1 | AHU
230 | hvac_floor1_duaFanAirHanUnit_mixingBox_mixBox_yRet_y | Return air damper position setpoint for AHU | 1 | AHU
231 | hvac_floor1_duaFanAirHanUnit_oveSpeRetFan_y | AHU return fan speed control signal | 1 | AHU
232 | hvac_floor1_duaFanAirHanUnit_supFan_oveSpeSupFan_y | AHU supply fan speed control signal | 1 | AHU
233 | hvac_floor1_duaFanAirHanUnit_supFan_variableSpeed_ovePreSetPoi_y | AHU supply fan static pressure setpoint | Pa | AHU
234 | hvac_floor1_fivZonVAV_vAV1_oveZonLoc_yDam_y | Damper position setpoint for zone cor | 1 | Zone Terminal
235 | hvac_floor1_fivZonVAV_vAV1_oveZonLoc_yReaHea_y | Reheat control signal for zone cor | 1 | Zone Terminal
236 | hvac_floor1_fivZonVAV_vAV2_oveZonLoc_yDam_y | Damper position setpoint for zone sou | 1 | Zone Terminal
237 | hvac_floor1_fivZonVAV_vAV2_oveZonLoc_yReaHea_y | Reheat control signal for zone sou | 1 | Zone Terminal
238 | hvac_floor1_fivZonVAV_vAV3_oveZonLoc_yDam_y | Damper position setpoint for zone eas | 1 | Zone Terminal
239 | hvac_floor1_fivZonVAV_vAV3_oveZonLoc_yReaHea_y | Reheat control signal for zone eas | 1 | Zone Terminal
240 | hvac_floor1_fivZonVAV_vAV4_oveZonLoc_yDam_y | Damper position setpoint for zone nor | 1 | Zone Terminal
241 | hvac_floor1_fivZonVAV_vAV4_oveZonLoc_yReaHea_y | Reheat control signal for zone nor | 1 | Zone Terminal
242 | hvac_floor1_fivZonVAV_vAV5_oveZonLoc_yDam_y | Damper position setpoint for zone wes | 1 | Zone Terminal
243 | hvac_floor1_fivZonVAV_vAV5_oveZonLoc_yReaHea_y | Reheat control signal for zone wes | 1 | Zone Terminal
244 | hvac_floor1_oveZonCor_TZonCooSet_y | Zone air temperature cooling setpoint for zone cor | K | Zone Terminal
245 | hvac_floor1_oveZonCor_TZonHeaSet_y | Zone air temperature heating setpoint for zone cor | K | Zone Terminal
246 | hvac_floor1_oveZonEas_TZonCooSet_y | Zone air temperature cooling setpoint for zone eas | K | Zone Terminal
247 | hvac_floor1_oveZonEas_TZonHeaSet_y | Zone air temperature heating setpoint for zone eas | K | Zone Terminal
248 | hvac_floor1_oveZonNor_TZonCooSet_y | Zone air temperature cooling setpoint for zone nor | K | Zone Terminal
249 | hvac_floor1_oveZonNor_TZonHeaSet_y | Zone air temperature heating setpoint for zone nor | K | Zone Terminal
250 | hvac_floor1_oveZonSou_TZonCooSet_y | Zone air temperature cooling setpoint for zone sou | K | Zone Terminal
251 | hvac_floor1_oveZonSou_TZonHeaSet_y | Zone air temperature heating setpoint for zone sou | K | Zone Terminal
252 | hvac_floor1_oveZonWes_TZonCooSet_y | Zone air temperature cooling setpoint for zone wes | K | Zone Terminal
253 | hvac_floor1_oveZonWes_TZonHeaSet_y | Zone air temperature heating setpoint for zone wes | K | Zone Terminal
254 | hvac_floor2_TSupAirSet_y | Supply air temperature setpoint for AHU | K | AHU
255 | hvac_floor2_dpSet_y | Supply duct pressure setpoint for AHU | Pa | AHU
256 | hvac_floor2_duaFanAirHanUnit_cooCoil_yCoo_y | Cooling coil valve control signal for AHU | 1 | AHU
257 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yEA_y | Exhaust air damper position setpoint for AHU | 1 | AHU
258 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yOA_y | Outside air damper position setpoint for AHU | 1 | AHU
259 | hvac_floor2_duaFanAirHanUnit_mixingBox_mixBox_yRet_y | Return air damper position setpoint for AHU | 1 | AHU
260 | hvac_floor2_duaFanAirHanUnit_oveSpeRetFan_y | AHU return fan speed control signal | 1 | AHU
261 | hvac_floor2_duaFanAirHanUnit_supFan_oveSpeSupFan_y | AHU supply fan speed control signal | 1 | AHU
262 | hvac_floor2_duaFanAirHanUnit_supFan_variableSpeed_ovePreSetPoi_y | AHU supply fan static pressure setpoint | Pa | AHU
263 | hvac_floor2_fivZonVAV_vAV1_oveZonLoc_yDam_y | Damper position setpoint for zone cor | 1 | Zone Terminal
264 | hvac_floor2_fivZonVAV_vAV1_oveZonLoc_yReaHea_y | Reheat control signal for zone cor | 1 | Zone Terminal
265 | hvac_floor2_fivZonVAV_vAV2_oveZonLoc_yDam_y | Damper position setpoint for zone sou | 1 | Zone Terminal
266 | hvac_floor2_fivZonVAV_vAV2_oveZonLoc_yReaHea_y | Reheat control signal for zone sou | 1 | Zone Terminal
267 | hvac_floor2_fivZonVAV_vAV3_oveZonLoc_yDam_y | Damper position setpoint for zone eas | 1 | Zone Terminal
268 | hvac_floor2_fivZonVAV_vAV3_oveZonLoc_yReaHea_y | Reheat control signal for zone eas | 1 | Zone Terminal
269 | hvac_floor2_fivZonVAV_vAV4_oveZonLoc_yDam_y | Damper position setpoint for zone nor | 1 | Zone Terminal
270 | hvac_floor2_fivZonVAV_vAV4_oveZonLoc_yReaHea_y | Reheat control signal for zone nor | 1 | Zone Terminal
271 | hvac_floor2_fivZonVAV_vAV5_oveZonLoc_yDam_y | Damper position setpoint for zone wes | 1 | Zone Terminal
272 | hvac_floor2_fivZonVAV_vAV5_oveZonLoc_yReaHea_y | Reheat control signal for zone wes | 1 | Zone Terminal
273 | hvac_floor2_oveZonCor_TZonCooSet_y | Zone air temperature cooling setpoint for zone cor | K | Zone Terminal
274 | hvac_floor2_oveZonCor_TZonHeaSet_y | Zone air temperature heating setpoint for zone cor | K | Zone Terminal
275 | hvac_floor2_oveZonEas_TZonCooSet_y | Zone air temperature cooling setpoint for zone eas | K | Zone Terminal
276 | hvac_floor2_oveZonEas_TZonHeaSet_y | Zone air temperature heating setpoint for zone eas | K | Zone Terminal
277 | hvac_floor2_oveZonNor_TZonCooSet_y | Zone air temperature cooling setpoint for zone nor | K | Zone Terminal
278 | hvac_floor2_oveZonNor_TZonHeaSet_y | Zone air temperature heating setpoint for zone nor | K | Zone Terminal
279 | hvac_floor2_oveZonSou_TZonCooSet_y | Zone air temperature cooling setpoint for zone sou | K | Zone Terminal
280 | hvac_floor2_oveZonSou_TZonHeaSet_y | Zone air temperature heating setpoint for zone sou | K | Zone Terminal
281 | hvac_floor2_oveZonWes_TZonCooSet_y | Zone air temperature cooling setpoint for zone wes | K | Zone Terminal
282 | hvac_floor2_oveZonWes_TZonHeaSet_y | Zone air temperature heating setpoint for zone wes | K | Zone Terminal
283 | hvac_floor3_TSupAirSet_y | Supply air temperature setpoint for AHU | K | AHU
284 | hvac_floor3_dpSet_y | Supply duct pressure setpoint for AHU | Pa | AHU
285 | hvac_floor3_duaFanAirHanUnit_cooCoil_yCoo_y | Cooling coil valve control signal for AHU | 1 | AHU
286 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yEA_y | Exhaust air damper position setpoint for AHU | 1 | AHU
287 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yOA_y | Outside air damper position setpoint for AHU | 1 | AHU
288 | hvac_floor3_duaFanAirHanUnit_mixingBox_mixBox_yRet_y | Return air damper position setpoint for AHU | 1 | AHU
289 | hvac_floor3_duaFanAirHanUnit_oveSpeRetFan_y | AHU return fan speed control signal | 1 | AHU
290 | hvac_floor3_duaFanAirHanUnit_supFan_oveSpeSupFan_y | AHU supply fan speed control signal | 1 | AHU
291 | hvac_floor3_duaFanAirHanUnit_supFan_variableSpeed_ovePreSetPoi_y | AHU supply fan static pressure setpoint | Pa | AHU
292 | hvac_floor3_fivZonVAV_vAV1_oveZonLoc_yDam_y | Damper position setpoint for zone cor | 1 | Zone Terminal
293 | hvac_floor3_fivZonVAV_vAV1_oveZonLoc_yReaHea_y | Reheat control signal for zone cor | 1 | Zone Terminal
294 | hvac_floor3_fivZonVAV_vAV2_oveZonLoc_yDam_y | Damper position setpoint for zone sou | 1 | Zone Terminal
295 | hvac_floor3_fivZonVAV_vAV2_oveZonLoc_yReaHea_y | Reheat control signal for zone sou | 1 | Zone Terminal
296 | hvac_floor3_fivZonVAV_vAV3_oveZonLoc_yDam_y | Damper position setpoint for zone eas | 1 | Zone Terminal
297 | hvac_floor3_fivZonVAV_vAV3_oveZonLoc_yReaHea_y | Reheat control signal for zone eas | 1 | Zone Terminal
298 | hvac_floor3_fivZonVAV_vAV4_oveZonLoc_yDam_y | Damper position setpoint for zone nor | 1 | Zone Terminal
299 | hvac_floor3_fivZonVAV_vAV4_oveZonLoc_yReaHea_y | Reheat control signal for zone nor | 1 | Zone Terminal
300 | hvac_floor3_fivZonVAV_vAV5_oveZonLoc_yDam_y | Damper position setpoint for zone wes | 1 | Zone Terminal
301 | hvac_floor3_fivZonVAV_vAV5_oveZonLoc_yReaHea_y | Reheat control signal for zone wes | 1 | Zone Terminal
302 | hvac_floor3_oveZonCor_TZonCooSet_y | Zone air temperature cooling setpoint for zone cor | K | Zone Terminal
303 | hvac_floor3_oveZonCor_TZonHeaSet_y | Zone air temperature heating setpoint for zone cor | K | Zone Terminal
304 | hvac_floor3_oveZonEas_TZonCooSet_y | Zone air temperature cooling setpoint for zone eas | K | Zone Terminal
305 | hvac_floor3_oveZonEas_TZonHeaSet_y | Zone air temperature heating setpoint for zone eas | K | Zone Terminal
306 | hvac_floor3_oveZonNor_TZonCooSet_y | Zone air temperature cooling setpoint for zone nor | K | Zone Terminal
307 | hvac_floor3_oveZonNor_TZonHeaSet_y | Zone air temperature heating setpoint for zone nor | K | Zone Terminal
308 | hvac_floor3_oveZonSou_TZonCooSet_y | Zone air temperature cooling setpoint for zone sou | K | Zone Terminal
309 | hvac_floor3_oveZonSou_TZonHeaSet_y | Zone air temperature heating setpoint for zone sou | K | Zone Terminal
310 | hvac_floor3_oveZonWes_TZonCooSet_y | Zone air temperature cooling setpoint for zone wes | K | Zone Terminal
311 | hvac_floor3_oveZonWes_TZonHeaSet_y | Zone air temperature heating setpoint for zone wes | K | Zone Terminal
312 | hvac_oveChiWatSys_TW_set_y | Chilled/hot water supply setpoint | K | Water Side
313 | hvac_oveChiWatSys_dp_set_y | Differential pressure setpoint | Pa | Water Side
314 | hvac_oveHotWatSys_TW_set_y | Chilled/hot water supply setpoint | K | Water Side
315 | hvac_oveHotWatSys_dp_set_y | Differential pressure setpoint | Pa | Water Side

## Sheet1
Energy Consumption (MJ)
| GDL36 | Baseline
hvac_floor1_readAhu_PFanSup_y | 2480.7464 | 4077.0112
hvac_floor2_readAhu_PFanSup_y | 25923.0647 | 40800.8219
hvac_floor3_readAhu_PFanSup_y | 2537.5849 | 3977.1165
hvac_reaChiWatSys_reaPChi_y | 34949.0513 | 40404.1591
hvac_reaChiWatSys_reaPCooTow_y | 159.6121 | 176.5252
hvac_reaChiWatSys_reaPPum_y | 25850.0659 | 23139.0995
hvac_reaHotWatSys_reaPBoi_y | 10393.3339 | 25326.9012
hvac_reaHotWatSys_reaPPum_y | 35.5106 | 35.4964
Total Energy Consumption | 102328.9697 | 137937.131
25.8148